## CAS Requirement
GOAL | Consolidated Alarm Solution to communicate with existing OPC servers of individual OEMs for communication to collect the alarms & events. The collected Alarm and Events to be presented on the operator PCs in most cases, be a real-time alarm table in a frame with scroll bars containing significant information for the operator. Presentation and Notification of Alarm: Solution should be able to display current alarm overview with all alarms that are active or not yet acknowledged and a historical alarm overview with all alarm status changes over time. Current alarms to be presented in a scalable frame with scrollbar controls that can, for example, be defined as a separate current alarm display. This overview may be dynamic by nature; if an alarm no longer exists and is acknowledged (manually or automatically), then the alarm should disappears from the screen. If there are no active alarms, this display is empty. Every column of the alarm text line should be able to be used to sort the alarms in the list by priority, time, status, etc. The historical alarm overview should have the same functionality as described above for the current alarm overview. In addition, all status changes of alarms should be represented in a fully scrollable historical alarm overview table with scroll bars and fast keys (page-up/down, and so on). Sequence of events recording: Both current and historical alarm displays should allow the display of sequences of event data coming from specialized equipment that can record and time-stamp events. Data should be shown in the right time-stamped order with a resolution down to a millisecond in-line with the OPC supports and supplies. Alarm lines should have colour and line formatting specific for this purpose. Events, because they are different from alarms, should be able to be shown separately when required.
Vendor
Requirement/Solution
OPC Communication/Connectivity - Using OPC A&E and/or DA
Honeywell OPC A&E Connectivity
Emerson OPC A&E Connectivity
Yokogawa OPC A&E Connectivity
Foxboro OPC A&E Connectivity (OEM is not providing the OPC A&E integration like other DCS vendors)
Matrikon OPC A&E Connectivity (Non-DCS)
Honeywell OPC DA Connectivity
Emerson OPC DA Connectivity
Yokogawa OPC DA Connectivity
Foxboro OPC DA Connectivity
Matrikon OPC DA Connectivity (Non-DCS)
Required Communication/Connectivity integration for non OPC A&E OEM's
Alternative Foxboro Integration (Via SQL) - Please also confirm Synchronisation time <= 5sec.
Communication / connectivity with AVEVA System Platform (wonderware) for Non-DCS alarms and events. Refresh < 5sec.
Future Communication/Connectivity requirements - Upcoming
ABB OPC A&E Connectivity
GE OPC A&E Connectivity
ABB OPC DA Connectivity
GE OPC DA Connectivity
Functional Requirements
Centralised near-real time alarm database. Update rate is between 5 to 10 sec.
One Alarm Banner Design including DC and non DCS alarms and events
Multi Alarm Banner Positions (1)
Adjustable and save-able filters by station(s), by priority, etc.
Configurable presetting's based on User login/Role for filters
Flexible Alarm Banner Integration with current IOC Platform (wonderware)
API availability to expose commands/control to and from current IOC Platform (Wonderware)
One single Alarm Database for analytics, reporting, dashboarding, Situational Awareness and user management/filtering
Architecture Requirements
Open Architecture with easy integration of CCTV, RDP, SQL, PI, Process Data, reports, Dashboards, etc.
Scalable solution in the existing PDO Infrastructure (OT/IT)
Integration/Usage of PI and/or SQL
Connection solution towards Baseera, Nibras and other third party software in PDO (PI and/or SQL)
One single string per OPC A&E Server to read to avoid network load and OPC Server load.
OPC A&E string should be filtered by the Consolidated Alarm Solution and maintain near-Realtime requirements
Simple configuration of the tags inside the alarm solution, inclusive simple exposure (no OPC-DA)
Please confirm if new DCS alarm added, does the solution update automatically the alarm database and banners.
Central Development/Decentral Deployment for optimal load and reduced network bandwidth usage
Technical Questions (Fill in the cells with proper information requested and provide documentation)
Number of servers required and what is their function
Provide a detailed System Architecture how it will be implemented in PDO PCD Domain
Are store and forward capabilities available when a server or network is down
Are backfill principles in place when a server or network is down
What software components are required to install your solution?
What are the configuration requirements for OPC A&E
What are the configuration requirements for IOC alarm banner by station
What are the system platform configuration requirements
Does your solution require to configure each alarm? If not, please explain the configuration principle for OPC A&E or other connectivity solutions
Please confirm no DCOM + OPC Tunneler will be used in your solution.
Does your architecture has a negative/positive impact on number of tags in System platform and why?
License Requirements
Unlimited Users
Unlimited Views/Screens/Banners/Dashboards/KPI's/Reports
Unlimited connections (OPC A&E, OPC DA, SQL, PI, etc.)
Unlimited Server Licenses
Unlimited Desktop Licenses
Subscription based Licensing (not preferred)
Perpetual based Licensing (preferred)
Annual Maintenance Framework (preferred)
Certifications, Resources and project timeline
Are there local certified resources in the Sultanate of Oman available to support and expand the solution?
What is the implementation timeline for your solution?