## CAS Clarification Register
PDO IOC — Consolidated Alarm Solution (CAS) ¦ Clarification & Requirements Register
74 sites · multi-vendor DCS (Honeywell / Emerson / Yokogawa / Foxboro / Matrikon; future ABB / GE) · Edge-to-Broker architecture · No DCOM / No OPC Tunneler. Questions to be issued to PDO and Yokogawa. Addressee: P = PDO, Y = Yokogawa, B = Both.
ID | Category | Question / Clarification Required | Why It Matters (Rationale) | Addressee | Priority | Response (to be completed by PDO / Yokogawa)
1. Scope & Requirements Clarification
1.1 | Scope & Requirements Clarification | The spec references integration with AVEVA System Platform / Wonderware (rows 17, 29, 30) and a System Platform tag-count impact (row 53), yet the current direction(as pe the dicussion yesterday with Mr. Girish) indicates this may be descoped in favour of standalone operator stations. Please confirm definitively: is AVEVA System Platform / IOC SCADA integration IN or OUT of scope? | This single answer reshapes the client UI, the licensing model and the System Platform tag-count requirement. It is the largest open variable in the design. | Both | Critical
1.2 | Scope & Requirements Clarification | Confirm the total number of DCS / OPC source systems across the 74 sites, broken down by OEM (Honeywell / Emerson / Yokogawa / Foxboro / Matrikon / other). | Drives the number of edge collectors, connector licences and total integration effort. | PDO | High
1.3 | Scope & Requirements Clarification | Are all 74 sites on one common PCD / OT network, or distributed across remote WAN links into the IOC? Please provide the network topology between sites, the CCR and the IOC. | Determines whether edge collectors publish to a single broker or to regional aggregation brokers, and the bandwidth/latency budget. | PDO | Critical
2. Architecture & the No-DCOM Constraint
2.1 | Architecture & the No-DCOM Constraint | To honour 'No DCOM and No OPC Tunneler', our edge-to-broker model needs the edge collector to run locally alongside each OPC A&E source (local COM, no remote DCOM). Are we permitted to install our lightweight edge agent directly on the existing OEM OPC A&E server or in a separate machine in the same layer? | Local installation is the direct technical consequence of the No-DCOM rule. | Both | Critical
2.2 | Architecture & the No-DCOM Constraint | If installing third-party software on the existing OPC server VM/server machine is prohibited by OEM warranty or PCD policy, what is the approved topology for local extraction — e.g. will PDO provision an adjacent VM/Server on the identical local subnet so the OPC connection remains local within the same layer? | If we cannot co-reside on the OPC server machine, PDO must provision adjacent edge server/VM | Both | Critical
2.3 | Architecture & the No-DCOM Constraint | Please confirm acceptance of the edge-to-broker pattern (MQTT / Sparkplug B over TLS) as the PCD-to-IOC transport, replacing DCOM and OPC tunnelling. | Confirms the foundational transport choice satisfies the No-DCOM/No-Tunneler requirement and cyber policy. | Both | High
2.4 | Architecture & the No-DCOM Constraint | Spec requires a 'single string per OPC A&E server'. Confirm this means one A&E subscription session per server, filtered at the edge — not per-tag DA polling. | Confirms the low-load, event-driven A&E subscription model the spec intends and avoids OPC-server overload. | Yokogawa | Medium
3. Infrastructure, Virtualization & PCD Compliance
3.1 | Infrastructure, Virtualization & PCD Compliance | Is deployment of Docker / Kubernetes (containerization) officially approved and supported within the PDO PCD? | Modern brokered architectures often containerize. the answer dictates the deployment model. | PDO | High
3.2 | Infrastructure, Virtualization & PCD Compliance | If containers are not approved, confirm we are limited to PDO-provided Windows Server / Linux VMs for the broker and central services, and state the standard OS builds/versions available. | Locks the supported deployment platform and OS baseline for sizing and compatibility. | PDO | High
3.3 | Infrastructure, Virtualization & PCD Compliance | What CPU / RAM / disk resources are available on the OPC A&E VMs (or adjacent edge VMs) to host the edge agent and buffer store-and-forward data during outages? | Required to size the local buffer for the mandated store-and-forward / backfill capability. | PDO | High
3.4 | Infrastructure, Virtualization & PCD Compliance | Will PDO provide the central / IOC compute (VMs, storage, database hosting), or must it be included in our offer? | Determines hardware scope and pricing for the central tier. | PDO | High
3.5 | Infrastructure, Virtualization & PCD Compliance | Confirm the virtualization/hypervisor standard in the PCD and IOC (VMware vSphere, Hyper-V, etc.) and any mandated hardening baseline | Ensures our components are certified/supported on the target platform and meet hardening rules. | PDO | Medium
4. Network & Cybersecurity
4.1 | Network & Cybersecurity | Is there a DMZ between the PCD/CCR and the IOC? Please provide the Purdue-level segmentation and the security zones the solution must traverse. | Defines where the broker bridge and any DMZ-resident services sit, and how many zone boundaries data crosses. | PDO | Critical
4.2 | Network & Cybersecurity | If acknowledgment from the IOC is required, can firewalls permit the specific bidirectional edge-to-broker path, or must acknowledgment be local-only at the DCS? | Confirms whether a controlled return channel is allowed or whether ack stays at the DCS. | Both | Critical
4.3 | Network & Cybersecurity | Which secure protocols and ports are approved by PDO cybersecurity for edge-to-broker traffic (e.g. MQTT over TLS 1.2/1.3 on port 8883)? | Firewall rules and the transport binding cannot be finalised without approved protocol/port. | PDO | High
5. Multi-Vendor OPC Connectivity & Data Handling
5.1 | Multi-Vendor OPC Connectivity & Data Handling | Provide each DCS platform with its exact OPC A&E (and DA where used) server product and version (Honeywell, Emerson, Yokogawa, Foxboro, Matrikon). | Connector compatibility and certified versions must be verified per OEM before commitment. | Both | High
5.2 | Multi-Vendor OPC Connectivity & Data Handling | Foxboro does not expose OPC A&E like the other DCS. Confirm the alternative integration is via SQL, provide the source schema, and confirm a synchronization time <= 5 s is achievable and acceptable. | Foxboro is the exception case; the SQL path and 5-second sync target must be validated against the actual schema. | Both | High
5.3 | Multi-Vendor OPC Connectivity & Data Handling | For Sequence of Events: must the CAS preserve the original millisecond timestamp generated at the lowest-level controller, and do all legacy OPC A&E servers actually pass this granular SOE timestamp (versus server-receive time)? | SOE fidelity depends on the source. If servers only pass receive-time, true ms SOE cannot be guaranteed and expectations must be reset. | Both | High
5.4 | Multi-Vendor OPC Connectivity & Data Handling | What time-synchronization source/standard (NTP / PTP) is used across the sites so cross-vendor SOE ordering is coherent? | Consistent time base is prerequisite for merging SOE from different OEMs into one ordered table. | PDO | Medium
5.5 | Multi-Vendor OPC Connectivity & Data Handling | Are alarm normalization / formatting rules required when consolidating events from disparate OEMs into one unified real-time alarm table (priority mapping, condition naming, area/asset model)? | Defines the normalization layer in the edge/central tier and the effort to map each OEM's model. | Both | Medium
5.6 | Multi-Vendor OPC Connectivity & Data Handling | When a new DCS alarm/tag is added, must the CAS alarm database and banners update automatically (auto-discovery), or is manual reconfiguration acceptable? (Spec row 40.) | Auto-discovery vs manual config materially changes design complexity and lifecycle effort. | Both | Medium
5.7 | Multi-Vendor OPC Connectivity & Data Handling | Future ABB and GE OPC A&E/DA connectivity is listed as upcoming. Confirm whether these must be included now (and priced) or are optional future phases. | Determines whether ABB/GE connectors are in the current commercial scope. | Both | Medium
5.8 | Multi-Vendor OPC Connectivity & Data Handling | Confirm whether OPC DA is genuinely required, or whether OPC A&E alone meets the alarm/event scope (spec row 39 prefers no OPC-DA exposure). | Avoids unnecessary DA polling load if A&E covers the requirement. | Both | Medium
6. Sizing & Performance
6.1 | Sizing & Performance | Peak alarm flood rate: expected worst-case alarms/second per site and aggregate at the IOC. | Drives edge buffer, broker throughput and database write sizing for the worst case. | Both | Critical
6.2 | Sizing & Performance | Steady-state and average event rates per site and aggregate. | Baseline capacity and storage growth planning. | Both | High
6.3 | Sizing & Performance | Concurrent users: number of simultaneous operator / engineer / viewer sessions at peak. | Sizes the web/UI tier and concurrent-session licensing. | PDO | High
6.4 | Sizing & Performance | Historical retention: required online retention period for alarms/events, plus archive and purge policy. | Sizes the historical store and defines archival design. | PDO | High
6.5 | Sizing & Performance | Confirm the near-real-time update target — the spec states 5-10 s, while other sections imply <= 5 s — and the acceptable end-to-end latency from DCS event to banner. | Resolves a conflicting requirement and sets the performance SLA the design must meet. | Both | High
6.6 | Sizing & Performance | Total tag/condition count per OPC server and aggregate across all sites.if available | Capacity planning for subscriptions, buffers and the alarm database. | Both | Medium
7. Standalone Operator Stations & UI
7.1 | Standalone Operator Stations & UI | With AVEVA integration potentially descoped, will PDO / Yokogawa supply the dedicated hardware and monitors for the standalone operator stations, or must client hardware be included in our offer? | Decides whether client hardware is a cost line in the commercial offer. | Both | High
7.2 | Standalone Operator Stations & UI | Exactly how many standalone operator stations are required across the Central Control Room and the IOC? | Sizes client deployment, licensing and commissioning effort. | PDO | High
7.3 | Standalone Operator Stations & UI | Preferred client deployment: a centralized web-based UI via standard browsers (Edge/Chrome), or a thick-client install? (We recommend web based.) | Sets the UI delivery model; Web based reduces per-station maintenance and avoids ActiveX/DCOM concerns. | Both | High
7.4 | Standalone Operator Stations & UI | If AVEVA remains in scope: must the banner be embedded as an ActiveX / HTML5 control inside the existing Wonderware HMI, or run as a standalone window? | Embedding constraints (especially ActiveX) significantly affect UI architecture. | Both | Medium
7.5 | Standalone Operator Stations & UI | Is Single Sign-On (e.g. Active Directory / LDAP) required for operator authentication, and which identity provider must we integrate with? | Defines authentication integration and the RBAC/role-based filter presets (spec row 28). | PDO | Medium
8. Integration (PI / SQL / Third-Party)
8.1 | Integration (PI / SQL / Third-Party) | Confirm the required integrations and direction for PI and/or SQL (read alarm data out only, or also write into CAS). | Defines the integration interfaces and data-flow direction with the historian/database layer. | Both | Medium
8.2 | Integration (PI / SQL / Third-Party) | Baseera, Nibras and other PDO third-party software — confirm the interface method (PI, SQL, REST API) and which systems are in scope. | Defines outbound integration adapters required for PDO's wider toolset. | PDO | Medium
8.3 | Integration (PI / SQL / Third-Party) | Is an open API required to expose commands/control to and from the IOC platform (spec row 30), and over which protocol (REST / OPC UA)? | Determines whether a published API layer is in scope and its protocol. | Both | Medium
8.4 | Integration (PI / SQL / Third-Party) | Confirm the CCTV / RDP integration referenced under 'open architecture' (spec row 33) — is this within CAS scope or handled display-side only? | Clarifies whether multimedia/RDP panes are a CAS deliverable. | PDO | Low
9. Redundancy, Availability & Backfill
9.1 | Redundancy, Availability & Backfill | Required availability / RPO / RTO for the central alarm database and broker (HA cluster, N+1, geo-redundancy)? | Sets the redundancy design and infrastructure count. | PDO | High
9.2 | Redundancy, Availability & Backfill | Confirm the store-and-forward buffer depth required at the edge — the maximum outage duration to survive with zero data loss — so local disk can be sized. | Directly sizes edge buffer storage for the mandated store-and-forward capability. | Both | High
9.3 | Redundancy, Availability & Backfill | On reconnection, must backfilled events be merged into history in correct SOE order using original timestamps? Confirm acceptable backfill behaviour. | Defines backfill correctness rules and history reconciliation logic. | Both | Medium
9.4 | Redundancy, Availability & Backfill | Is broker redundancy / clustering required, and is a DMZ-resident broker bridge to the IOC acceptable? | Confirms broker HA topology and placement relative to the DMZ. | Both | Medium
10. Licensing & Commercial
10.1 | Licensing & Commercial | Must licensing cover the future ABB / GE connectors and additional sites beyond the initial 74? | Determines whether future expansion is pre-licensed or chargeable later. | Both | Medium
10.2 | Licensing & Commercial | Confirm currency, payment milestones, and the warranty / support period expected for the commercial offer. | Required to structure the commercial proposal. | PDO | Medium
11. Resources, Support & Project Execution
11.1 | Resources, Support & Project Execution | Are locally certified resources required in the Sultanate of Oman for support and future expansion (spec row 64), and is In-Country Value (ICV) a scoring criterion? | Affects resourcing model, partnerships and bid scoring. | PDO | Medium
11.2 | Resources, Support & Project Execution | Confirm the required implementation timeline and any mandated milestones, including FAT/SAT requirements (spec row 65). | Sets the project schedule and acceptance gates. | Both | High